## Sheet1
Contractor or Supplier Action or Requirement | Inspection or Procedure Required
Must have Arizona State Fire Marshall approved Fire Alarm
Shop Drawings. | Must have pre-installation meeting with PD&C electrical inspector.
Install all Fire Alarm raceway and junction boxes. | Must have PD&C electrical inspection before proceeding.
Device layout inspection. | Must have PD&C electrical inspection with FM and/or Risk Management.
Receive Fire Alarm wiring and splicing class. | Must receive this before proceeding.
Install and pull all fire alarm wire. All loops must be wired thru
to check integrity. | Must have PD&C electrical inspection before proceeding.
Meter all loops from Fire Alarm Panel box to check for opens,
shorts, crossed circuits, and ground faults on all wiring. | Must have PD&C electrical inspection before proceeding.
Receive device addresses printed on drawings from Fire
Alarm supplier. | Must receive this before proceeding.
Install/connect all Fire Alarm devices for this project, to
include pulls,smokes, heats, ducts, a/v's, v/o's, horns,
bells, sprinkler monitors, all shutdown connections,
and any other Fire Alarm related equipment. | Must have PD&C electrical or FM Fire Safety inspection before proceeding.
Meter all loops from Fire Alarm Panel box to check for opens, | Must have PD&C electrical inspection with FM Fire Safety
shorts, crossed circuits, and ground faults on all wiring. | before proceeding.
Have Fire Alarm supplier install panel components and land
field wiring, and trim out panel.Provide UofA with signal | Must have PD&C electrical inspection or FM Fire Safety approval
circuit loads,total stand by load and alarm load calculations. | before proceeding.
Fire alarm supplier must provide proposed control software and
device/circuit labels to UofA Fire Safety for approval before
installation of software in Fire Alarm Control Panel. | Must receive approval from Fire Safety before proceeding.
Contractor and supplier must successfully complete a NFPA 72
test before calling for a UofA Fire Safety, contractor and | Provide copy of contractor / supplier NFPA 72 test to PD&C to call for
supplier NFPA 72 test to start commissioning run. | UofA NFPA 72 test.
Contractor, supplier and UofA Fire Safety must successfully
complete a NFPA 72 test before the five day | A NFPA 72 test witnessed by UofA Fire Safety must be completed with
commissioning run will start. | no deviations before starting commissioning run.
After the successful completion of the commissioning run, then | UofA Fire Safety will confirm the commissioning run has completed with
the State Fire Marshall Test can occur. | no troubles, supervisories or alarms.
Contractor, supplier, UofA Fire Safety, and Risk Management
will be involved with the State Fire Marshall Test. | PD&C / Risk Management will schedule the State Fire Marshall Test.